Gas filling stand for COMPASS
(located in the cellar)

What must be remote controlled and what information about the actual state of the controlled part (and even not controlled, but for the operation important) is to disposal:
1. 2 pieces of rotary pumps;
2. 1 piece of turbomolecular pump (TMP);
3. 13 pieces of electrically controlled (every two wires for solenoid 24V DC/0.2A), but by pressurized air driven valves with electrical signalization of the actual valve position (another two wires: valve is closed – wires are disconnected , valve is open – wires are connected), see CV1, CV2, V1-V9, V13, V14 in the figure below;
4. 3 pieces of electrically controlled (7-pins connector, pins 1 and 2 – feeding of solenoid by 24V DC/0.2A), by pressurized air driven valves, with electrical signalization of the actual valve position (valve is open → pins 3 and 4 are connected; moreover the position is visible also by eyes), see V10, V11, V12 in the figure below;
5. 4 pieces of Mass-Flow Controllers (controlled voltage 0-5V, connected through 15-pin connector).
Note: In addition, 5 pieces of mechanically handled valves with any position signalization
        are also used in the vacuum scheme, see mech1-5 in the figure below.

The vacuum will measured using 7 vacuum gauges with digital output:
5 pieces of piezo gauges CPT-100 (1-2000mbar)
2 Pirani gauges PPT-100 (10-4-1000mbar)

Prague, 9.1.2008